## Public Health Sewage (Code) Regulations 2008

COOK ISLANDS

PUBLIC HEALTH SEWAGE (CODE) REGULATIONS 2008
________

Sir F. Goodwin, KBE

Queen's Representative

ORDER IN EXECUTIVE COUNCIL

At Avarua, Rarotonga, this 4th day of December 2008

Present:

HIS EXCELLENCY THE QUEEN'S REPRESENTATIVE IN EXECUTIVE COUNCIL

PURSUANT to Sections 41 and 42 of the Public Health Act 2004 the Queen's Representative, acting by and with the advice and consent of the Executive Council, makes the following regulations.

__________

ANALYSIS

1. Title and commencement
2. Prescribed code
Schedule

_________

REGULATIONS

1. Title and commencement - (1) These regulations may be cited as the Public Health Sewage (Code) Regulations 2008.

(2) These regulations shall come into force on the 1st day of November 2008.

2. Prescribed Forms - The prescribed Code is as set out in the Schedule to these regulations.

Grover L. Harmon

Clerk of the Executive Council

_________
These Regulations are administered by Ministry of Public Health
__________________

SCHEDULE

Cook Islands

Te Marae Ora Ministry of Health

Public Health Sewage Code

Community Health Services Directorate
Ministry of Health
PO Box 109
Rarotonga
Cook Islands

July 2008

Contents

|  | AMENDMENTS |
| --- | --- |
| 1.0 | POLICIES |
| 1.1 | Processing of Sewage Construction Permit Applications on Each Islands |
| 1.2 | Referenced Documents |
| 2.0 | GUIDELINES AND STANDARDS |
| 2.1 | Fees |
|  | 2.1.1 | Application for a Sewage Construction Permit - Regulation 19 (2) (f) |
| 2.2 | Definition of Lagoon Protection Zone |
| 2.3 | Land Information Memorandum (Drainage) |
| 2.4 | Zone Implementation of the Regulations |
| 2.5 | Alternative wastewater management systems |
| 2.6 | Septic Tank Capacities (litres) |
|  | 2.6.1 | For 1 - 10 persons |
|  | 2.6.2 | For 11 - 20 persons |
|  | 2.6.3 | For more than 20 persons |
| 2.7 | Sludge Removal |
|  | 2.7.1 | Frequency of desludging - Regulation 33 (1) |
|  | 2.7.2 | Sludge Removal Reports - Regulation 33 (2) |
| 2.8 | Sewage Flow Reporting |
|  | 2.8.1 | Moderate Load System - Regulation 28 (2) |
|  | 2.8.2 | High Load System - Regulation 28 (2) |
| 2.9 | Sampling Frequencies |
|  | 2.9.1 | Moderate Load Systems - Regulation 30 (2) |
|  | 2.9.2 | High Load Systems - Regulation 30 (2) |
| 2.10 | Testing Procedure |
| 2.11 | Wastewater Flow Design Allowances |
| 2.12 | Classification of Buildings |
| 2.13 | Positioning of the Land Application System |
| 2.14 | Soil Classification |
| 2.15 | Appearance and Feeling of Various Soil Textural Classes |
| 2.16 | Setbacks |
| 2.17 | Design Specification of Land Application System |
| 2.18 | Drain laying Standards |
| 2.19 | Treatment Unit Categories and Effluent Quality Standards |
| 2.20 | Effluent outlet filters |
| 2.21 | Noise |
| 2.22 | Septic Tank Construction Standards |
| 2.23 | Sewage Discharge Standards |
| 3.0 | TIME PERIODS |
| 3.1 | Request for Sewage System Inspection - Regulation 21 (3) and 21 (5) |
| 4.0 | REGISTERS |
| 4.1 | Register of Sanitary Professionals and Technicians - Regulation 7 |
|  | 4.1.1 | Criteria for Installers and Servicing Agents |
|  | 4.1.2 | Criteria for the Registration of Inspectors |
|  | 4.1.3 | Criteria for the Registration of Designers |
| 4.2 | Register of Sewage Treatment Unit Designs - Regulation 9 |
|  | 4.2.1 | Criteria for the Registration of Sewage Treatment Unit Designs |
|  | 4.2.2 | Aeration treatment plants |
|  | 4.2.3 | Applications for the Registration of Sewage Treatment Unit Designs – Regulation 9 (2) |
| 4.3 | Register of Septic Tank Manufacturers - Regulation 8 |
|  | 4.3.1 | Criteria for the Registration of Septic Tank Manufacturers |
| 5.0 | REPORTS |
| 5.1 | Abandonment or Disconnection Plan - Regulation 31 |
| 5.2 | Operation and Maintenance Manual - Regulation 29 |

Amendments

| Previous Version (January 2008) | Current Version (July 2008) |
| --- | --- |
| SECTION 1.1 PROCESSING OF SEWAGE CONSTRUCTION PERMIT APPLICATIONS ON EACH ISLAND | SECTION 1.1 PROCESSING OF SEWAGE CONSTRUCTION PERMIT APPLICATIONS ON EACH ISLAND |
| Section 1.1 Processing of Sewage Construction Permit Applications on Each Island previously read as follows: It is important that applications for sewage construction permits be made (as much as possible) on the island where the sewage system is being installed. This is because the approval process requires some knowledge of the site conditions such as soil permeability, baserock/impermeable layers of the soil profile, groundwater depth etc. Health Inspectors on each island will need to have a C1 pass in the Sewage and Sanitation Course. For those islands where a C1 pass hasn't been achieved, the application will need to be processed in Rarotonga. In addition, applications for Moderate Load and High Load systems are more complex and will require additional knowledge during the approval process. For this reason, applications for Moderate Load and High Load systems on all islands shall be made in Rarotonga in consultation with the Health Inspectors on the respective island. Before the regulations are promulgated, Public Health will implement this code under Section 13 of the Public Health Act 2004 as a policy document. During this period, the code will apply to the following properties only: 1. Properties where the land application system is located within the Lagoon Protection Zone 2. Properties that will require a Moderate or High Load system In all other cases, septic tanks to AS/NZS 1546.1 standards and absorption trenches or soak holes shall be sufficient until promulgation of the regulations. | Section 1.1 Processing of Sewage Construction Permit Applications on Each Island previously read as follows: It is important that applications for sewage construction permits be made (as much as possible) on the island where the sewage system is being installed. This is because the approval process requires some knowledge of the site conditions such as soil permeability, baserock/impermeable layers of the soil profile, groundwater depth etc. Health Inspectors on each island will need to have a C1 pass in the Sewage and Sanitation Course. For those islands where a C1 pass hasn't been achieved, the application will need to be processed in Rarotonga. In addition, applications for Moderate Load and High Load systems are more complex and will require additional knowledge during the approval process. For this reason, applications for Moderate Load and High Load systems on all islands shall be made in Rarotonga in consultation with the Health Inspectors on the respective island. |
| Previous Version (January 2008) | Current Version (July 2008) |
| SECTION 1.2 REFERENCED DOCUMENTS | SECTION 1.2 REFERENCED DOCUMENTS |
| Section 1.2 Referenced Documents previously read as follows: 1.2 Referenced Documents The following documents are referenced in this code: Public Health (Sewage) Regulations 2008 | Section 1.2 Referenced Documents now reads as follows (changes are shown in bold): 1.2 Referenced Documents The following documents are referenced in this code: Public Health (Sewage) Regulations 2008 |
| AS/NZS 1547:2000 On-site domestic-wastewater management AS/NZS 3500 National plumbing and drainage code AS/NZS 1546.1:1998 On-site domestic wastewater treatment units Part 1: Septic tanks Copies of documents b, c and d may be purchased online at www.standards.co.nz . Copies of the Public Health Sewage Regulations 2008 may be purchased from the Community Health Services Directorate, Ministry of Health, Tupapa, Rarotonga. | AS/NZS 1547:2000 On-site domestic-wastewater management AS/NZS 3500 National plumbing and drainage code New Zealand Building Code G13 Foul Water and E1 Surface Water AS/NZS 1546.1:2008 On-site domestic wastewater treatment units Part 1: Septic tanks AS/NZS 1546.2:2008 Waterless Composting Toilets AS/NZS 1546.3:2008 Aerated Wastewater Treatment Systems Copies of documents listed in d. may be downloaded free from http://www.dbh.govt.nz/building-code-compliance-documents#free-download. Copies of documents b, c e, f, g may be purchased at www.standards.co.nz. Copies of the Public Health (Sewage) Regulations 2008 may be purchased from Parliament Services, Rarotonga, Cook Islands |
| Previous Version (January 2008) | Current Version (July 2008) |
| SECTION 2.2. DEFINITION OF LAGOON PROTECTION ZONE | SECTION 2.2 DEFINITION OF LAGOON PROTECTION ZONE |
| Section 2.2 Definition of Lagoon Protection Zone regarding the LPZ of Aitutaki previously read as follows: The Lagoon Protection Zone on Aitutaki is located where the soil type is sand. | Section 2.2 Definition of Lagoon Protection Zone regarding the LPZ of Aitutaki now reads as follows (changes are shown in bold): The Lagoon Protection Zone on Aitutaki is located where the soil type is either category 1, 2, 5 or 6 as described in AS/NZS 1547:2000. |
| Previous Version (January 2008) | Current Version (July 2008) |
| SECTION 2.4 ZONE IMPLEMENTATION OF THE REGULATIONS | SECTION 2.4 ZONE IMPLEMENTATION OF THE REGULATIONS |
| Section 2.4 Zone Implementation of the Regulations previously read as follows: The principles of AS/NZS 1547:2000 and the specifications described in Table 1 shall be used when designing a sewage system. In cases where the specifications in Table 1 are contradictory to the specifications in AS/NZS 1547:2000, the specifications in Table 1 shall override the specifications in AS/NZS 1547:2000. | Section 2.4 Zone Implementation of the Regulations now reads as follows (changes are shown in bold): The principles of AS/NZS 1547:2000 and the specifications described in Table 1 shall be used when designing a sewage system. In cases where the specifications in Table 1 are contradictory to the specifications in AS/NZS 1547:2000, the specifications in Table 1 shall override the specifications in AS/NZS 1547:2000. Due to the density of development within Avarua town, Avarua town has been earmarked for the development of a sewerage system. For this reason, Table 1 shall apply to all areas of Rarotonga except for Avarua town (between the western side of Avatiu harbour and the eastern side of the National Auditorium, Library and Museum and between the back road of Avarua and seaward side of the foreshore). Persons owning properties within Avarua Town shall meet standards in the Public Health Sewage Regulations and Public Health Sewage Code as closely as is practicable. |
| Previous version (January 2008) | Current Version (July 2008) |
| SECTION 2.6 SEPTIC TANK CAPACITIES | SECTION 2.6 SEPTIC TANK CAPACITIES |
| Section 2.6, Tables 2-4 regarding septic tank capacities previously read as follows: Table 2: All-Waste Sept Tank Capacities Number of persons Average daily flow (litres) Tank capacity (litres) 1-5 Up to 1000 3000 6-7 1000-1400 3500 8 1400-1600 4000 9-10 1600-2000 4500 Table 3: Greywater Septic Tank Capacities Number of Persons Average daily flow (litres) Tank capacity (litres) 1-5 Up to 600 1800 6-7 600-840 2100 8 840-960 2400 9-10 960-1200 2700 Table 4: Blackwater Septic Tank Capacities Number of persons Average daily flow (litres) Tank capacity (litres) 1-5 Up to 300 1500 6-7 300-420 1800 8 420-480 2100 9-10 480-600 2500 | Section 2.6, Tables 2-4 regarding septic tank capacities will now reads as follows: Table 2: All-Waste Sept Tank Capacities Number of persons Average daily flow (litres) Tank capacity (litres) 1-10 Up to 2000 4500 Table 3: Greywater Septic Tank Capacities Number of Persons Average daily flow (litres) Tank capacity (litres) 1-5 Up to 600 1800 6-10 600-1200 2700 Table 4: Blackwater Septic Tank Capacities Number of persons Average daily flow(litres) Tank capacity (litres) 1-5 Up to 300 1500 6-10 300-600 2500 |
| Previous Version (January 2008) | Current Version (July 2008) |
| Section 2.18 DRAIN LAYING STANDARDS | SECTION 2.18 DRAIN LAYING STANDARDS |
| Section 2.18 Drain laying Standards, previously read as follows: 2.18 Drain laying Standards Regulation 15(7) All drain laying shall be according to AS/NZS 3500 National plumbing and drainage code standards. | Section 2.18 drain laying Standards, now reads as follows (changes are shown in bold): 2.18 drain laying Standards Regulation 15(7) All drain laying shall be accordance with the AS/NZS 3500 National plumbing and drainage code standards, and the New Zealand Building Code E1 Surface Water and G13 Foul Water standards. |
| Previous Version (January 2008) | Current Version (July 2008) |
| SECTION 2.19 TREATMENT UNIT CATEGORIES AND EFFLUENT QUALITY STANDARDS | SECTION 2.19 TREATMENT UNIT CATEGORIES AND EFFLUENT QUALITY STANDARDS |
| Section 2.19 Treatment Unit Categories and Effluent Quality Standards, previously read as follows: 2.19 Treatment Unit Categories and Effluent Quality Standards Regulation 15(4) As a guide, raw sewage has a biochemical oxygen demand (BOD5) and Total Suspended Solids of TSS of 300 - 400 mg/litre and a faecal coliform count of 1010-107 cfu/100ml Table 9: Treatment Unit Categories and Effluent Quality Standards Treatment level Effluent standards Primary treatment BOD5-90% of samples taken over three test periods shall not exceed 180mg/litre and no sample shall exceed 200mg/litre TSS-90% of samples taken over three test periods shall not exceed 80mg/litre and no sample shall exceed 100mg/litre FC-the median value shall be no more than 107 cfu/100ml and no sample shall exceed 108 cfu/100ml. Secondary treatment BOD5- 90% of samples taken over three test periods shall not exceed 20mg/litre and no sample shall exceed 30mg/litre TSS-90% of samples taken over three test periods shall not exceed 30mg/litre and no sample shall exceed 45mg/litre. FC- Where disinfection is provided, the samples taken on each occasion shall have a thermotolerant coliform count not exceeding a median value of 10 organisms per 100ml with 80% of the samples containing less than 20 organisms per 100ml and no sample exceeding 100 organisms per 100ml. Where disinfection is not provided, the samples taken on each occasion shall have a thermotolerant coliform count not exceeding a median value of 104 organisms per 100ml with 80% of the samples containing less than 105 organisms per 100ml and no sample exceeding 106 organisms per 100ml. TN-90% of samples shall not exceed 40mg/litre and no sample shall exceed 60 mg/litre Where chlorination is the disinfection process, the total chlorine concentration shall be greater than or equal to 0.5mg/litre in four out of five samples taken. Advanced treatment BOD5-90% of samples taken over three test periods shall not exceed 10mg/litre and no sample shall exceed 20mg/litre TSS-90% of samples taken over three test periods shall not exceed 10mg/litre and no sample shall exceed 20mg/litre FC-The samples taken on each occasion shall have a thermotolerant coliform count not exceeding a median value of 10 organisms per 100ml with 80% of the samples containing less than 20 organisms per 100ml and no sample exceeding 100 organisms per 100ml. TN-90% of samples taken over three test periods shall not exceed 15mg/litre and no sample shall exceed 20mg/litre TP-90% of samples taken over three test periods shall not exceed 10mg/litre and no sample shall exceed 15mg/litre Where chlorination is the disinfection process, the total chlorine concentration shall be greater than or equal to 0.5mg/litre in four out of five samples taken. | Section 2.19 Treatment Unit Categories and Effluent Quality Standards, now reads as follows (changes are shown in bold): 2.19 Treatment Unit Categories and Effluent Quality Standards Regulation 15(4) As a guide, raw sewage has a biochemical oxygen demand (BOD5) and Total Suspended Solids of TSS of 300 - 400 mg/litre and a faecal coliform count of 1010-107 cfu/100ml Samples shall be collected over one test period consisting of three consecutive days during peak flow on each day (and in the case of visitor accommodation, during 75% to 100% capacity) as outlined in section 2.10 "Testing Procedure" in this Sewage Code. Table 9: Treatment Unit Categories and Effluent Quality Standards Treatment level Effluent standards Primary treatment BOD5-90% of samples shall not exceed 180mg/litre and no sample shall exceed 200mg/litre TSS-90% of samples shall not exceed 80mg/litre and no sample shall exceed 100mg/litre FC-the median value shall be no more than 107 cfu/100ml and no sample shall exceed 108 cfu/100ml. Secondary treatment BOD5-90% of samples shall not exceed 20mg/litre and no sample shall exceed 30mg/litre TSS-90% of samples shall not exceed 30mg/litre and no sample shall exceed 45mg/litre. FC- Where disinfection is provided, the samples taken on each occasion shall have a thermotolerant coliform count not exceeding a median value of 10 organisms per 100ml with 80% of the samples containing less than 105 organisms per 100ml and no sample exceeding 106 organisms per 100ml. TN-90% of samples shall not exceed 40mg/litre and no sample shall exceed 60mg/litre Where chlorination is the disinfection process, the total chlorine concentration shall be greater than or equal to 0.5mg/litre in four out of five samples taken. Advanced treatment BOD5-90% of samples shall not exceed 10mg/litre and no sample shall exceed 20mg/litre TSS-90% of samples shall not exceed 10mg/litre and no sample shall exceed 20mg/litre FC- The samples taken on each occasion shall have a thermotolerant coliform count not exceeding a median value of 10 organisms per 100ml with 80% of the samples containing less than 20 organisms per 100ml and no sample exceeding 100 organisms per 100ml. TN-90% of samples shall not exceed 15mg/litre and no sample shall exceed 20mg/litre TP-90% of samples shall not exceed 5mg/litre and no sample shall exceed 10mg/litre Where chlorination is the disinfection process, the total chlorine concentration shall be greater than or equal to 0.5mg/litre in four out of five samples taken. |

| Previous Version (January 2008) | Current Version (July 2008) |
| --- | --- |
| SECTION 4.1 REGISTER OF SANITARY PROFESSIONALS AND TECHNICIANS | SECTION 4.1 REGISTRY OF SANITARY PROFESSIONALS AND TECHNICIANS |
| Section 4.1 Register of Sanitary Professionals and Technicians previously read as follows: 4.1 Register of Sanitary Professionals and Technicians 4.1.1 Criteria for the Registration of Installers and Servicing Agents For the first year of implementation of the regulations, the criteria for the registration of installers and servicing agents shall be: A national certificate in plumbing or drainlaying from New Zealand or Australia or a qualification equivalent to the requirements set out by the Master Plumbers, Gasfitters and Drainlayers NZ Inc. Industry Training Organisation for a national certificate in plumbing and drainlaying. After the first year of implementation of the regulations, the criteria shall be: Both a pass in the CET training programme, Category 3 and a national certificate in plumbing or drainlaying from New Zealand or Australia or a qualification equivalent to the requirements set out by the Master Plumbers, Gasfitters and Drainlayers NZ Inc Industry Training Organisation for a national certificate in plumbing and drainlaying. 4.1.2 Criteria for the Registration of Inspectors For the first year of implementation of the regulations, the criteria for the registration of inspectors shall be: Pass in the CET Sewage and Sanitation Course Category 1 AND Be able to demonstrate experience with and knowledge of the drainlaying and plumbing trade After the first year of implementation of the regulations, the criteria shall be: A pass in the CET Sewage and Sanitation Course Category 1 and a national certificate in plumbing or drainlaying from New Zealand or Australia or a qualification equivalent to the requirements set out by the Master Plumbers, Gasfitters and Drainlayers NZ Inc. Industry Training Organisation for a national certificate in plumbing and drainlaying. 4.1.3 Criteria for the Registration of Designers Pass in the CET Sewage and Sanitation Course Category 2 AND An appropriate engineering or applied science degree or diploma Exemptions: There will be some applicants who will consider that they have qualifications and experience in sanitation equivalent to, or of a higher standard than, the qualifications specified above. The Board will consider applications from such professionals and tradespeople. The applicant will be required submit details of the qualifications and experience. Applications should be made to: Sanitary Planner Ministry of Health PO Box 109 Rarotonga The application is to include the following details: Name Contact details Formal qualifications with details of the institution certifying the qualification Details of professional registration Membership of professional and/or trade bodies Summary of experience in sanitation engineering Details of experience within the Cook Islands Contact details for three professional and/or industry referees The Board reserves the right to require the applicant to sit an assessment paper. | Section 4.1 Register of Sanitary Professionals and Technicians now reads as follows: 4.1 Register of Sanitary Professionals and Technicians-Regulation 7 4.1.1 Criteria for Installers and Servicing Agents The registration of installers and servicing Agents shall not take effect until 1st October 2009. Until that time, the Sewage and Sanitation Board shall retain a list of Approved Installers and Servicing Agents who are qualified to install and service septic tanks and other sewage treatment systems. The criteria for Approved Installers and Servicing Agents are: 1) A National Certificate in Drainlaying (Level 4) from an NZQA accredited institution* in New Zealand or a similar institution in Australia AND 2) At least two years of practical experience supervised by a drainlayer registered in New Zealand or Australia AND 3) Has completed a short course, set and approved by the Board, on the Public Health (Sewage) Regulations 2008 and the Public Health Sewage Code 2008 (the CET Sewage and Sanitation Course held in Rarotonga, Cook Islands 2006-2007 qualifies for this requirement) Discretionary Approval Applicants who do not meet criteria 1) but who have a qualification in drainlaying from an institution outside of New Zealand or Australia may apply for the discretionary approval. Applicants who do not meet criteria 2) and/or 3) may not be registered by the Sewage and Sanitation Board. Application for discretionary approval are to include the following details: 1) Name 2) Contact details 3) Formal qualifications with full contact details of the institution certifying the qualification 4) Details of professional registration (type of license, license number, name and full contact details of the authority issuing the license) 5) Membership of professional and/or trade bodies (if any) and their full contact details 6) Summary of experience in drain laying 7) Details of experience within the Cook Islands (if any) 8) Full contact details for three professionals and/or industry referees 9) Full contact details for three clients for jobs completed within the last three years 10) Notarized copy of formal qualifications and birth certificate The Sewage and Sanitation Board reserves the right to require the applicant to sit an assessment paper and/or to have their work assessed by a New Zealand /Australian Registered drainlayer. A listing as an Approved Installer and/or Servicing Agent will become void upon 1st October 2009. Registration of Installers and Servicing Agents (Septic Tanks) After 1st October 2009, Public Health will only approve the installation of primary treatment systems (septic tanks) that are installed by Cook Islands Registered Installers of septic tanks. Furthermore, after 1st October 2009, only Cook Islands Registered Servicing Agents of primary treatment systems (septic tanks) will be permitted to service septic tanks. The criteria for Registered Installers and Servicing Agents of septic tanks are the same criteria used to determine Approved Installers and Servicing Agents (outlined in 1-3 above). Registration for installers and servicing agents of septic tanks who receive registration on or after 1st October 2009 will be valid until 1st October 2010. Thereafter, annual renewal of registration will be required and will be due on the 1st October of each year. Registration of Installers and servicing agents (Secondary/Advanced Sewage Treatment Systems) After 1st October 2009, Public Health will only approve the installation of Secondary /Advanced treatment systems that are installed by Cook Islands Registered Installers of Secondary/Advanced treatment systems. Furthermore, after 1st October 2009, only Cook Islands Registered Servicing Agents of Secondary/Advanced treatment systems will be permitted to service Secondary/Advanced treatment systems. The criteria for Registered Installers of Secondary/Advanced treatment systems are the same criteria used to determine Approved Installers and Servicing Agents (outlined in 1-3 above) with the ADDITIONAL criterion which shall be: 4) Has been trained and certified by the manufacturers of the Secondary/Advanced treatment system as an installer and servicing agent for the respective model of that treatment system. Registration for installers and Servicing Agents of Secondary/Advanced treatment systems who receive registration on or after 1st October 2009 will be valid until 1st October 2010. Thereafter, annual renewal of registration will be required and will be due on the 1st October of each year. *accredited institutions which provide this qualification in New Zealand are: Christchurch Polytechnic Institute of Technology UniTec New Zealand Waikato Institute of Technology Wellington Institute of Technology Plumbing, Gasfitting and Drainlaying ITO Ltd. 4.1.2 Criteria for the Registration of Inspectors Between 31st January 2008 and 1st October 2009, the criteria for the registration of inspectors are: 1) The applicant has obtained a pass in the exams for the CET Sewage and Sanitation Course Category 1 AND 2) The applicant has submitted at least one CET Stage 3 project and received a pass for that project AND 3) The applicant is able to demonstrate experience with and knowledge of the drainlaying and plumbing trade Registration for inspectors who are registered during this period will be valid for 12 months from the date of approval. After 1st October 2009, the criteria for the registration of inspectors are: 1) The applicant has a pass in the CET Sewage and Sanitation Course Category 1 AND 2) The applicant has a certificate for Drainlaying Theory Assessment from an NZQA accredited institution in New Zealand or an equivalent institution in Australia or a qualification equivalent to the requirements set out by the Master Plumbers, Gasfitters and Drainlayers NZ Inc. Industry Training Organisation for a Certificate for Drainlaying Theory Assessment." Registration for inspectors who are registered during this period will be valid for 12 months from the date of approval. 4.1.3 Criteria for the Registration of Designers Between 31st January 2008 and 1st October 2009, the criteria for the registration of designers are: 1) The applicant has obtained a pass in the exams for the CET Sewage and Sanitation Course Category 2 AND 2) The applicant has submitted at least one CET Stage 3 project and received a pass for that project AND 3) The applicant has an appropriate engineering or applied science degree or diploma Registration for designers who are registered during this period will be valid for 12 months from the date of approval. After 1st October 2009, the criteria for the registration of designers are: 1) The applicant has obtained a pass in the CET Sewage and Sanitation Course Category 2 AND 2) The applicant has an appropriate engineering or applied science degree or diploma Registration for designers who are registered during this period will be valid for 12 months from the date of approval. Exemptions: There will be some applicants who will consider that they have qualifications and experience in sanitation equivalent to, or of a higher standard than, the qualifications specified above. The Board will consider applications from such professionals and tradespeople. The applicant will be required to submit details of their qualifications and experience. Applications should be made to: Health Planner (Sanitation) Ministry of Health PO Box 109 Rarotonga The application is to include the following details: 1) Name 2) Contact details 3) CET or similar course(s) attended including year and venue of each course 4) Any other formal qualification with details of the institution certifying the qualification 5) Details of professional registration, if any 6) Details of any membership of professional and/or trade bodies 7) Summary of experience insanitation engineering 8) Details of experience within the Cook Islands 9) Contact details for three professional and/or industry referees The Board reserves the right to require the applicant to sit an assessment paper. |

1.0 Policies

1.1 Processing of Sewage Construction Permit Applications on Each Island

It is important that applications for sewage construction permits be made (as much as possible) on the island where the sewage system is being installed. This is because the approval process requires some knowledge of the site conditions such as soil permeability, baserock/impermeable layers of the soil profile, groundwater depth etc. Health Inspectors on each island will need to have a Cl pass in the Sewage and Sanitation Course. For those islands where a Cl pass hasn't been achieved, the application will need to be processed in Rarotonga. In addition, applications for Moderate Load and High Load systems are more complex and will require additional knowledge during the approval process. For this reason, applications for Moderate Load and High Load systems on all islands shall be made in Rarotonga in consultation with the Health Inspectors on the respective island.

1.2 Referenced Documents

The following documents are referenced in this code:

a) Public Health (Sewage) Regulations 2008

b) AS/NZS 1547:2000 On-site domestic-wastewater management

c) AS/NZS 3500 National plumbing and drainage code

d) New Zealand Building Code G13 Foul Water and E1 Surface Water

e) AS/NZS 1546.1:2008 On-site domestic wastewater treatment units Part 1: Septic tanks

f) AS/NZS 1546.2:2008 Waterless Composting Toilets

g) AS/NZS 1546.3:2008 Aerated Wastewater Treatment Systems

Copies of documents listed in d. may be downloaded free from http://www.dbh.govt.nz/building-code-compliance-documents#free-download. Copies of documents b, c, e, f, g may be purchased at www.standards.co.nz. Copies of the Public Health (Sewage) Regulations 2008 may be purchased from Parliament Services, Rarotonga, Cook Islands.

2.0 Guidelines and Standards

2.1 Fees

2.1.1 Application for a Sewage Construction Permit-Regulation 19(2)(f)

Fees will cover the costs of a site visit prior to approval of the sewage construction permit, the assessment of the application and a site visit to inspect the system after it is connected and before it is covered. Moderate and High Load Systems will require additional expert assessment.

| Low Load Systems: | $55 |
| --- | --- |
| Moderate Load Systems: | $200 |
| High Load Systems: | $500 |

Should another site visit be needed, the owner will be required to submit an additional request for sewage system inspection and pay an additional fee.

| Additional Requested Sewage System Inspection: | $25 |
| --- | --- |

2.2 Definition of Lagoon Protection Zone

Regulation 3

The Lagoon Protection Zone is an area where higher standards of sewage treatment are needed to protect the coastal lagoon from sewage pollution.

The Lagoon Protection Zone on Rarotonga is located around the coast and is defined by those areas where the soil type is characterised as Koromiri soils, Mauri soils stony phase, Vaikai soils and Vaikai soils mottled phase. Application for Sewage Construction Permits on Vaikai Soils and Vaikai Soils mottled phase may frequently be declined due to the vulnerability of the sewage system to flooding in these zones.

The Lagoon Protection Zone on Aitutaki is located where the soil type is either category 1,2,5 or 6 as described in AS/NZS 1547:2000.

For those properties where the boundary of the Lagoon Protection Zone cuts through the property, the location of the effluent land application area within the property shall determine whether or not the sewage system is located within the Lagoon Protected Zone. If the effluent land application area is within the Lagoon Protection Zone, then the sewage system shall follow the rules for sewage systems located within the Lagoon Protection Zone.

2.3 Land Information Memorandum (Drainage)

Regulation 13 (1) and (2), 19(5) (b) (iii)

The purpose of a Land Information Memorandum (Drainage) is to maintain information on every sewage system inspected after the commencement of the Regulations. This information is valuable for managing the regulation of sewage at the individual property level as well as at a greater scale such as the village level. The Public Health Department is responsible for maintaining the Land Information Memorandum (Drainage) for each property. Upon the sale or transfer of a property, a copy of the Land Information Memorandum (Drainage) must be made available to the public upon request.

A land Information Memorandum (Drainage) may include details such as the ownership fo the system, type of system, date of installation, desludging record, capacity, design loading, plans of tanks, land application system and other fixtures and seasonal high groundwater table depth in the effluent land application area, proximity to surface water, soil type at effluent land application area, post-treatment disposal method and any system maintenance contract pertaining to that system including results of tests and inspections conducted on the system.

2.4 Zone Implementation of Regulations

The principles of AS/NZS 1547:2000 and the specifications described in Table 1 shall be used when designing a sewage system. In cases where the specification in Table 1 are contradictory to the speicifications in AS/NZS 1547:2000, the specification in Table 1 shall override the specifications in AS/NZS 1547:2000.

Due to the density of development within Avarua town, Avarua town has been earmarked for the development of a sewage system. For this reason, Table 1 shall apply to all areas of Rarotonga except for Avarua town (between the western side of Avaitu harbour and seaward side of the National Auditorium, Library and Museum and between the back road of Avarua and seaward side of the foreshore). Persons owning properties within Avarua town shall meet standards in the Public Health Sewage Regulations and Public Health Sewage Code as closely as is practicable.

Table 1: Zone Implementation of the Regulations

Stage 1 (first 3 years of implementation of Regulations)

|  | Wastewater system load |
| --- | --- |
|  | Low load <2000L/day | Moderate load 2,000 to 10,000 litres per day | High load >10,000 litres per day |
| Lagoon protection zone LPZ | Existing Over the next 3 years retrofit septic tanks with approved septic tank filters during maintenance and inspections. New, failed1 or alteration to existing buildings: • Primary treatment with septic tank filter or better. • Soak pits prohibited • Dose loading to land application system. • Land application to trench or mound with loading rates in accordance with AS/NZS 1547:2000 • For those choosing secondary treatment, subsurface irrigation is permitted with DIR to be less than 8 mm/day Land application performance criteria • <1000FC cfu/100mls at 1m below point of entry to land. • No surface ponding or liquid breakout • No odours • Must meet required setbacks as in code | Existing By the 3rd year start upgrading to advanced treatment levels • with land applications to achieve <1000FC cfu at 1m below point of entry to land. • >50% TN removal 1m below the point of entry to land, within 3 years New, failed or alteration to existing • Advanced treatment • Land application to subsurface irrigation to be less than 8 mm/day Land application performance criteria • <1000FC cfu/100ml at 1m below point of entry to land. • 50% TN removal 1m below point of entry to land • No odours • No surface ponding • Must meet required setbacks as in code Monitoring • Monitor and submit flow data as in Reg. 28(2) • Performance monitoring as in Reg. 30 beginning 3 years from commencement of regulations | Existing Over the next 3 years, upgrade to advanced treatment levels with land application to achieve • <1000FC cfu at 1m below point of discharge • >50% TN removal 1m below the point of entry to land, within 2 years. New, failed or alteration to existing • Advanced treatment • Land application to trench or mound with loading rate less than 50mm/day • Land application to subsurface irrigation to be less than 8 mm/day Land application performance criteria • <1000FC cfu/100mls at 1m below point of entry to land. • 75% TN removal 1m below point of entry to land. • 50% TP removal 1m below point of entry to land • No odours • No surface ponding • Must meet required setbacks as in code. Monitoring • Monitor and submit flow data as in Reg 28(2) • Performance monitoring as in Reg 30 beginning 3 years from commencement of regulations • Provide implementation and facility plans (Reg 16) |
| Note 1: Within the next 3 years, all property owners (including those with an existing system) are to be provided with user friendly operators manual, appropriate to their system type. |
| Note 2: Failed means any system that repeatedly results in any of the following failure modes: system blockages, flooding, ponding, health risk, nuisance odours and/or significant ecosystem damage. |
| Wastewater system load |
|  | Low load <2000L/day | Moderate load 2,000 to 10,000 litres per day | High load >10,000 litres per day |
| Outside LPZ., sandy soils | Existing Over the next 3 years retrofit septic tanks with approved septic tank filters during maintenance and inspections New, failed or alterations to existing buildings: • Primary treatment with septic tank filter or better. •Soak pits permitted if groundwater is greater than 6m below ground level • Dose loading to land application system. • Land application to trench, mound with loading rate less than 50mm/day • For those choosing secondary treatment, subsurface irrigation is permitted with DIR to be less than 8 mm/day Land application performance criteria • <1000FC cfu at 900mm below point of discharge. • No surface ponding or liquid breakout • No odours • Must meet required setbacks as in code unless land area is limited in which case a higher level of treatment is required | Existing Over the next 3 years upgrade to advanced treatment levels with land application to achieve • <1000FC cfu at 1m below point of entry to land. New, failed or alteration to existing • Advanced treatment • Land application to trench or mound with loading rate less than 50mm/day • Land application to subsurface irrigation to be less than 8 mm/day Land application performance criteria • <1000FC cfu at 1m below point of entry to land. • 50% TN removal 1m below point of entry to land. • No odours • No surface ponding • Must meet required setbacks as in code Monitoring • Monitor and submit flow data as in Reg 28(2) • Performance monitoring as in Reg 3 beginning 3 years from commencement of regulations | Existing Over the next 3 years, upgrade to advanced treatment levels with land application to achieve • < 1000FC cfu at 900mm below point of discharge • 50% TN removal 900mm below the point of entry to land within 3 years New, failed or alteration to existing • Advanced treatment • Land application to trench or mound with loading rate less than 50mm/day • Land application to subsurface irrigation to be less than 8mm/day Land application performance criteria • <1000FC cfu at 1m below point of entry to land. • 75% TN removal 1m below point of entry to land. • 50% TP removal 1m below point of entry to land. • No odours • No surface ponding • Must meet required setbacks as in code • Provide implementation and facility plans (Reg 16) Monitoring • Monitor and submit flow data as in Reg 28(2) • Performance monitoring as in Reg 3 beginning 3 years from commencement of regulations |
| Note 1: Within the next 3 years, all property owners (including those with an existing system) are to be provided with user friendly operators manual, appropriate to their system type. |
| Note 2: Failed means any system that repeatedly results in any of the following failure modes: system blockages |

|  | Low load <2000L/day | Moderate load 2,000 to 10,000 litres per day | High load >10,000 litres per day |
| --- | --- | --- | --- |
| Outside LPZ., with moderately draining soils | Existing Over the next 3 years retrofit septic tanks with approved septic tank filters during maintenance and inspections. New, failed or alterations to existing buildings: • Primary treatment with septic tank filter or better. • Soak pits subject to hydraulic soakage testing. • Land application to trench, mound or ET bed with loading rate in accord with AS/NZS 1547 criteria. • For those choosing secondary treatment, subsurface irrigation is permitted with DIR to be less than 4 mm/day. Land application performance criteria • <1000FC cfu/100ml at 1m below point of entry to land. • No surface ponding or liquid breakout • No odours • Must meet required setbacks as in code unless land area is limited in which case a higher level of treatment is required | Existing Over the next 3 years upgrade to advanced treatment levels with land application to achieve: • <1000FC cfu at 1m below point of entry to land. New, failed or alteration to existing • Advanced treatment • Land application to trench, mound or ET bed with loading rate in accord with AS/NZS 1547 criteria. • Subsurface irrigation is permitted with DIR to be less than 4 mm/day. Land application performance criteria • <1000FC cfu at 1m below point of entry to land. • 50% TN removal 1000 mm below the point of entry, •No odours • No surface ponding • Must meet required setbacks as in code Monitoring • Monitor and submit flow data as in Reg 28(2) • Performance monitoring as in Reg 3 beginning 3 years from commencement of regulations | Existing Over the next 3 years, upgrade to advanced treatment levels with land application to achieve • <1000FC cfu at 1m below point of entry to land. • 50% TN removal 1m below point of entry to land. New, failed or alteration to existing • Advanced treatment • Land application to trench, mound or ET bed with loading rate in accord with AS/NZS 1547 criteria. • Subsurface irrigation is permitted with DIR to be less than 4mm/day Land application performance criteria • <1000FC cfu at 1m below point of entry to land. • 75% TN removal 1m below point of entry to land. • 50% TP removal 11m below point of entry of land. • No odours • No surface ponding • Must meet required setbacks as in code. • Provide implementation and facility plans (Reg 16) Monitoring • Monitor and submit flow data as in Reg 28(2) • Performance monitoring as in Reg 3 beginning 3 years from commencement of regulations |
| Note 1: Within the next 3 years, all property owners (including those with an existing system) are to be provided with user friendly operators manual, appropriate to their system type. |
| Note 2: Failed means any system that repeatedly results in any of the following failure modes: system blockages |
|  | Low load <2000L/day | Moderate load 2,000 to 10,000 litres per day | High load >10,000 litres per day |
| Outside LPZ with poorly draining soils | Existing Over the next 3 years retrofit septic tanks with approved septic tank filters during maintenance and inspections. New, failed or alterations to existing buildings: • Primary treatment with septic tank filter or better. • Soak pits prohibited • Land application to trench, mound or ET bed with loading rate in accord with AS/NZS 1547 criteria. • For those choosing secondary treatment, subsurface irrigation is permitted with DIR to be less than 3mm/day. Land application performance criteria • <1000FC cfu at 900mm below point of discharge. • No surface ponding or liquid breakout • No odours • Must meet required setbacks as in code unless land area is limited in which case a higher level of treatment is required | Existing Over the next 3 years upgrade to advanced treatment levels with land application to achieve: • <1000FC cfu at 1m below point of point of entry to land. New, failed or alteration to existing • Advanced treatment • Land application to trench, mound or ET bed with loading rate in accord with AS/NZS 1547 criteria. • Subsurface irrigation is permitted with DIR to be less than 3 mm/day. Land application performance criteria • <1000FC cfu at 1m below point of point of entry to land. • 50% TN removal 1m below point of point entry to land. • No odours • No surface ponding • Must meet required setbacks as in code Monitoring • Monitor an d submit flow data as in Reg 28(2) • Performance monitoring as in Reg 3 beginning 3 years from commencement of regulations | Existing Over the next 3 years, upgrade to advanced treatment levels with land application to achieve • <1000FC cfu at 1m below point of point of entry to land. • 50% TN removal 1m below point of point of entry to land. New, failed or alteration to existing • Advanced treatment • Land application to trench, mound or ET bed with loading rate in accord with AS/NZS 1547 criteria. •Subsurface irrigation is permitted with DIR to be less than 3mm/day Land application performance criteria •<1000FC cfu at 1m below point of point of entry to land. •75% TN removal 1m below point of point of entry to land. •50% TP removal 1m below point of point of entry to land. •No odours • No surface ponding • Must meet required setbacks as in code • Provide implementation and facility plans (Reg 16) Monitoring • Monitor and submit flow data as in Reg 28(2) • Performance monitoring as in Reg 3 beginning 3 years from commencement of regulations |
| Note 1: Within the next 3 years, all property owners (including those with an existing system) are to be provided with user friendly operators manual, appropriate to their system type. |
| Note 2: Failed means any system that repeatedly results in any of the following failure modes: system blockages, flooding, ponding, health risk, nuisance odours and/or significant ecosystem damage. |

2.5 Alternative wastewater management systems

There may be proposals that depart from the specification above. For example; stream separation systems (such as greywater, blackwater, urine), dry systems such as composting toilets and greywater treatment using constructed wetlands. These will be admissible to the Board, as special cases, for approval and will be assessed against the following criteria:

Applicants will be required to clearly demonstrate the following, using scientific evidence and principles, and in the context of Cook Islands social and biophysical conditions

• Site conditions for example:

▪Is the proposal within the lagoon protection zone? - more stringent performance criteria will be imposed.
▪Is the proposal site on free draining soils with high water table?
▪Is the proposal on poorly draining soils?

• Very low health risk to users, neighbours, community, lagoon users over the life of the service.
• Very low risk of impact on connected land and water ecosystems in terms of ecosystem goods, services, and products and integrity of habitats over the life of the service
• Very low risk of nuisance factors, over the life of the service, such as

▪ Odours
▪ Noise
▪ Visual

• Efficient resource use, particularly energy.
• System resilience to variable loading (i.e. variable daily/seasonal quality and quantity)
• Affordability, including annual costs over the life of the system

Additionally the application should, where appropriate, be supported with the following documentation

• System specifications including system capacity (average and short-term peak loading)
• Scaled drawing of system
• Test performance results (preferably from an independent and certified testing agency
• Independent system certification by an approved agency:
• Operator/owner manual
• Servicing and maintenance manual
• Warranty details
• Designer producer statement
• List of 3 to 4 referees

All systems will be required to meet required setbacks as specified in the Code

For moderate and high load systems

• Monitor and submit flow data as in Regulation 28(2)
• Performance monitoring as in Regulation 30

2.6 Septic Tank Capacities (litres)

2.6.1 FOR 1 - 10 PERSONS

All-Waste Septic Tank Capacities

The minimum capacity tank for any all-waste domestic wastewater on-site application is recommended to be 4500 litres. This provides for approximately a 24-hour settling volume for a daily flow of up to 2000 litres from an equivalent population of up to 10 persons, and 2500 litres scum-and sludge-storage capacity providing for a maximum interval prior to desludging/pumpout of 3 years. A 5-year desludging/pumpout interval would require a 6000 litre tank.

Tank capacities are shown in Table 2.

Table 2: All-Waste Sept Tank Capacities

| Number of persons | Average daily flow(litres) | Tank capacity (litres) |
| --- | --- | --- |
| 1-10 | Up to 2000 | 4500 |

Greywater Septic Tank Capacities

The minimum capacity tank for any domestic greywater on-site application is recommended to be 1800 litres.

The 1800 litre greywater tank allows for approximately a 24-hour settling volume plus an allowance of 8 hours hydraulic buffering volume for the daily greywater flows from 5 persons. About 1000 litres capacity is allowed for sludge and scum accumulation over a 5-year period.

Minimum sizes are given in Table 3.

Table 3: Greywater Septic Tank Capacities

| Number of Persons | Average daily flow (litres) | Tank capacity (litres) |
| --- | --- | --- |
| 1-5 | Up to 600 | 1800 |
| 6-10 | 600-1200 | 2700 |

Blackwater Septic Tank Capacities

The minimum capacity tank for any domestic blackwater on-site application is recommended to be 1500 litres.

The 1500 litre blackwater tank allows for approximately a 24-hour settling volume for the daily water-closet flows of 5 persons. About 1200 litres capacity is allowed for scum and sludge accumulation over a 5-year period.

Minimum sizes are given in Table 4.

Table 4: Blackwater Septic Tank Capacities

| Number of persons | Average daily flow (litres) | Tank capacity (litres) |
| --- | --- | --- |
| 1-5 | Up to 300 | 1500 |
| 6-10 | 300-600 | 2500 |

2.6.2 FOR 11-20 PERSONS

For 11-20 persons (inclusive), the capacity C of a septic tank shall be determined by the following formula provided that the total flow does not exceed 2,000litres/day on any day:

C = (P x A) + 2000 litres

Where P = the number of persons to be served and A = the daily wastewater flow allowance in litres/person/day as outlined in Table 5 "Wastewater Flow Design Allowances"

2.6.3 FOR MORE THAN 20 PERSONS

If the flow is calculated to be more than 2,000 litres per day, primary treatment and then drainage to a land application system is not permitted. Advanced treatment is required for flows of more than 2,000 litres per day.

2.7 Sludge Removal

2.7.1 Frequency of desludging-Regulation 33 (1)

Septic tanks should be desludged either

(a) Every three to five years OR

(b) When the scum layer (layer of crust on top) comes down to within 100mm of the bottom of the tee junction or filter at outlet OR

(c) When the sludge (build up of material on bottom of tank) and scum have accumulated to the extent that the scum and sludge take up 2/3 of the volume of the tank's first chamber

whichever occurs first.

2.7.2 Sludge Removal Reports - Regulation 33 (2)

A sludge removal contractor shall submit a sludge removal report to the Public Health Department within 30 days of desludging a septic tank.

An example of a Sludge Removal Report is shown in the Appendix.

2.8 Sewage Flow Reporting

2.8.1 Moderate Load System - Regulation 28(2)

The owner of a Moderate Load System shall submit data on sewage flow to the Public Health Department on an annual basis. A graph of the daily volume of sewage produced on the property for that year shall be included in the sewage flow report.

2.8.2 High Load System - Regulation 28(2) 

The owner of a High Load System shall submit data on sewage flow to the Public Health Department on an annual basis. A graph of the daily volume of sewage produced on the property for that year shall be included in the sewage flow report.

2.9 Sampling Frequencies

2.9.1 Moderate Load Systems - Regulation 30(2)

Beginning three years after the date of commencement of the regulations, and at a frequency of once every three years the owner of a Moderate Load System shall sample effluent from their sewage system in the manner described in 2.10 below and have the samples tested in an accredited laboratory for BOD5 (mg/l), TSS (mg/l), FC (cfu/100ml), TN (mg/l), TP (mg/l).

2.9.2 High Load Systems - Regulation 30(2)

Beginning three years after the date of commencement of the regulations, and at a frequency of once every three years the owner of a High Load System shall sample effluent from their sewage system in the manner described in 2.10 below and have the samples tested in an accredited laboratory for BOD5 (mg/l), TSS (mg/l), FC (cfu/100ml), TN (mg/l), TP (mg/l).

2.10 Testing Procedure

1. The sewage system shall be assembled, installed and operated in accordance with the manufacturer's instructions. Prior to testing, a certified and registered servicing agent shall inspect the sewage system to ensure it is operating as it should.

2. The raw influent shall not be pre-treated by chemical addition and as a guideline should have the characteristics as set out in the table below:

Table 5: Characteristics of raw influent

| Component | Characteristic |
| --- | --- |
| BOD5 | 150-300 mg/litre |
| TSS | 150-300 mg/litre |
| Total nitrogen | 20-100 mg/litre |
| Total phosphorus | 6-25 mg/litre |

3. There shall be two testing periods:

Test period 1: before the primary treatment chamber is desludged
Test period 2: nine weeks after test period 1

4. The hourly flow rate shall be recorded in litres per hour. A higher flow rate is expected between 6am and 11am and 6pm and 9pm.

5. The tests required are as follows:

(a) Raw wastewater: BOD5, TSS, TN, TP

(b) During test period: BOD5, TSS, FC, DO, disinfectant levels (if applicable)

(c) TN and TP

(d) Ambient temperature and liquid temperature inside the secondary treatment tank or chamber

6. Sampling points are as follows:

(a) Samples for BOD5, TSS shall be taken from the disinfection/irrigation chamber

(b) The final effluent samples for FC and disinfectant levels (if applicable) shall be taken from the outlet of the treatment unit

(c) Samples for DO shall be taken from the aeration chamber (if applicable)

7. The samples shall be transported to an accredited laboratory for analysis within 24 hours of sampling.

8. Samples are to be analysed in accordance with a method specified in one of the following texts or references:

(a) Standards Methods for Examination of Water and Wastewater, 18th edition (1992), or more recent editions or supplements as they become available;

(b) Relevant Australian Standards published by Standards Australia, as amended or varied from time to time or other method that has been demonstrated to provide equivalent results;

(c) Relevant New Zealand Standards published by Standards New Zealand as amended or varied from time to time

9. The effluent compliance criteria are given in Table 9.

10. Test Period Procedure

For three days the following tests shall be performed under the supervision of a Sanitary Inspector during peak flow (normally peak flow is between 6am and 11am and between 6pm and 9pm) and again during the lowest flow period of daylight hours.

Table 6: Test Period Procedure

| Time interval | Action |
| --- | --- |
| 00 min | Adjust flow to 30 litres/person/HOUR |
| 30 min | Sample for BOD5 TSS, FC and measure DO and disinfectant |
| 60 min | Sample for BOD5, TSS, FC and measure |
|  | DO and disinfectant |
| 90 min | Sample for BOD5, TSS,, FC and measure DO and disinfectant |
| 120 min | Sample for BOD5, TSS, FC and measure Do and disinfectant, and then adjust flow to 600 litres/hour |
| 150 min | Measure disinfectant, and FC and adjust to normal flow |

2.11 Wastewater Flow Design Allowances

The occupancy allowances and design flow allowances for wastewater flow design shown in Tables 7 and 8 are adapted from Chapter Six of the Auckland Regional Council Technical Publication 58 (TP58). The occupancy allowances and design flow allowances in AS/NZS 1547:2000 shall not apply in the Cook Islands.

Table 7: Occupancy Allowances

| Facility | Occupancy for Design Purposes |
| --- | --- |
| Homes |
| Number of Bedrooms (Notes 1, 2 & 3) 1 2 3 4 5 6 | 2 4 5 6 8 9 |
| Hotels and Motels |
| Guests Staff | Maximum Occupancy/Number of beds Maximum Staff |
| Hospitals (Note 4) |
| Patients Staff | 1 per bed (Note 3) Maximum Number of Staff |
| Notes: 1. It is usual to adopt a minimum occupancy of 4 persons (equivalent to a 2 bedroom dwelling) for existing rural residential cluster developments. 2. In situations where large modern dwellings are proposed which have additional rooms beyond those allocated as dining, lounge, bedrooms, e.g. "family", "recreation", "games", "office", "study", "sewing", "work", rooms) which could have potential to be utilised as bedrooms with different furnishings, an additional occupancy is to be made on the basis of 1 extra person times the ratio of the total floor area of the additional room(s) to that of the smallest designated bedroom and rounded up to the next whole number. 3. Design occupancy should allow for a seasonal peak, not just the average daily flow. Holiday homes tend to have intermittent occupancy but when occupied are likely to have a higher occupancy than a continuously occupied dwelling. An allowance in design occupancy should be made for the seasonally higher flows. 4. Occupancy data in this table is from the literature and observed levels. A higher water use/person should be allowed in facilities providing community care unless specific water meter data is available. 5. In the event that the designer does not design for the predicted flow from the full potential occupancy, it will be necessary to record wastewater discharge flows and submit to Public Health. |

Table 8: Wastewater Flow Allowances - Per Capita

| Source | Typical Wastewater Flow Allowance |
| --- | --- |
|  | Litres/Person/Day | (Note 1 and Note 2) |
|  | On-site Roof Water Tank Supply | Reticulated Community or Bore Water Supply |
| Flow Allowances |
| A. Upmarket Luxury Households with Extra Wastewater producing fixtures including fixtures such as garbage grinders, dishwashers, modern shower or bath facilities or other comparable fixtures | 220 | 220 |
| B. Households with Standard Fixtures including 11 litre flush water cisterns; automatic washing machine and dishwasher [Note 5] | 180-200 | 200 |
| C. Households with 11/5.5 or 6/3 Flush Toilet(s) and Standard Fixtures, low water use dishwasher and NO garbage grinder [Note 6] | 160 | 180 |
| I. Households - Blackwater Only (Based on an 11 litre flush toilet) [Note 7] | 66 |
| J. Households - Blackwater Only (Based on a 11/5.5 flush toilet) | 45 |
| K. Households - Blackwater Only (Based on a 11/5.5 flush toilet) | 25 |
| L. Households - Greywater Only (with Extra Water Reduction Fixtures) [Note 8] | 95 to 100 | 100 to 115 |
| Commercial Flow Allowances for Standard Fixtures |
| Motels/Hotels [Note 9] - Guests, resident staff - Reception rooms - Bar trade (per customer) - Restaurant (per diner) | 220 30 15 to 20 30 |
| Restaurant/Bar/Café [Note 10] - Per dinner patron - Per lunch patron - Per bar patron | 30 25 15 to 20 |
| Lunch Bar (per customer) - Without restroom facilities - With restroom facilities | 10 15 | 15 25 |
| Community Halls - Banqueting - Meetings | 20 10 | 30 15 |
| Hostels [Note 11] - Day only visitors - Day plus overnight visitors | 40 150 |
| Schools (pupils plus staff) [Note 12] | 12 to 15 | 15 to 20 |
| Public Toilets (including hand wash) [Note 13] | 10-20 | 10-20 |
| Camping Grounds [Note 14] - Fully serviced - Recreation areas | 100 50 | 130 65 |
| Rest Homes/Hospitals [Note 15] | 220 | 250 |
| Retirement Home - Per Resident [Note 15] - Per Day Staff | 200 40 | 220 50 |
| Day Staff - High Water Usage e.g. some factories [Note 16] - For ALL Standard Facilities (above) | 60 40 |
| Notes: 1. These flows are recommended minimums for design purposes (unless actual comprehensive water usage/flow records along with actual occupancy numbers are available). In some instances ranges of design flow rates are provided to reflect the inherent uncertainty associated with actual per capita wastewater production. 2. Where a site is reliant on water being supplemented by water tanker, the design flow allowances based on reticulated water supply must be applied. 3. Use of the following household flow allowances apply to on-site system designs for dwellings with special approval from the Sewage and Sanitation Board. 4. Extra Wastewater producing fixtures include fixtures such as garbage grinders; dishwashers, modern shower or bath facilities or other comparable fixtures. 5. These include 11 litre flush water cisterns; automatic washing machine and dishwasher. No garbage grinder unless other water saving measures such as low flush 6/3 litre toilet cisterns. 6. Standard Fixtures include dual flush 11/5.5 or 6/3 litre toilet cisterns, and includes standard automatic washing machine, but a low water use dishwasher, no garbage grinder. 7. Flow rates to be applied where only the blackwater from toilets is to be treated and discharged to land disposal. 8. Flow rates to be applied where only the greywater is to be treated and discharged to land disposal. The lower design flow is only to be applied where there is no bath. Applicable where solids from kitchen and toilet waste flows are excluded from the wastewater stream. For households with low water use facilities in accordance with Note 6, the lower end of the range applies; for standard household domestic facilities, the higher range applies [see Note 8]. *At the time of printing, trade names of effective FOFC devices include Trident and Jemflow. 9. Evidence does not support lower water usage by staff or guests of commercial premises, so no differentiation is made to the flow allowances according to the water supply source. Some reduction (up to 25%) may apply to the per guest water usage allowance if laundry, is undertaken off-site. 10. Evidence does not support lower water usage between roof water a and reticulated water supplies usage by staff or guests of commercial premises, so no differentiation is made to the flow allowances according to the water supply source. For bar patrons, it is assumed that there is minimal if any food served, other than odd bar snacks. Where meals are served, meal water usage allocations apply per patron. In bar facilities, where water full reduction fixtures are installed on all water usage outlets and patrons are only present for short periods, a water usage allowance of 10 litres per person may be appropriate. 11. Assumes that lunches and lunch/dinners will be served, and that overnight visitors have access to showers but not to laundry facilities. Water meter readings should be installed to provide added certainty to the accuracy in the design flow allowance. The designer should be aware that water conservation measures installed in commercial premises eg; bars, restaurants may not provide the same level of savings as achieved by domestic uses. Unless specific metered water consumption information is available conservative flow allowances should be applied 12. Based upon experience in the Auckland area, these values for schools are conservative. Recorded flows appear to be up to 15 litres/person/day on rainwater tank supply, and 15 to 20 litres/person/day on community or borewater supply. For design purposes, figures from the lower end of the range should be supported by accrual water usage records otherwise the higher figure should be used. Additional allowances also need to be made in the design flows for schools that also have cafeteria (with on-site catering) and/or gyms with shower facilities. 13. For low water use toilets with 6/3 litre flush cisterns, standard public toilets, the lower end of the range applies; for modern upmarket toilet facilities, the higher range applies. 14. Recreation areas with no showers or communal cooking facilities. 15. Flow allowances for individual dwelling within a retirement village may be based on the recommended flow allowances for households or alternatively on flow meter rates where these are available. Where extra care facilities are provided the actual per capita rates will be higher than standard rates provided and a conservative design allowance should be applied. 16. Increased water usage allowances are appropriate where staff activities likely to involve regular cleaning of themselves and/or the facilities e.g. rural food preparation factory. Where staff are likely to use showers, the designer should consider all the activities being undertaken by staff and rates higher than 60 litres per person per day may apply. |

2.12 Classification of Buildings

Regulation 25 (4)

An understanding of the nature of wastewater from a particular building can be gained by collecting information on the type of building that the sewage system will serve. This information can also help to manage situations where a sewage system is designed for one particular class of building but the use of the building is later changed and the sewage system can no longer cope with the new wastewater flow (for example converting a residential house into a restaurant). Under the Public Health (Sewage) Regulations 2008, no person shall change the use of their building in such a way that the new use will result in additional sewage flow without the permission of the Public Health Department (Regulation 25 (2)). A person is changing the use of a building when the new use will result in the placement of the building in a different class. Therefore, during the application process for a Sewage Construction Permit or Sewage System Modification Permit, every building that is served by a sewage system must be declared as being of a particular class or combination of classes. Classes of use are as follows:

A Residential House
B Tourist Accommodation Rental
C Long Term Accommodation Rental
D Office
E Bar
F Restaurant/Cafe
G School
H Factory
I Public toilet
J Service station
K Retail store
L Laundry
M Gymnasium
N Laboratory
O Hospital
P Health Clinic
Q Entertainment centre
R Church
S Community hall

2.13 Positioning of the Land Application System

The Land Application System shall be positioned:

(i) to maximize the distance between the outlets of the land application system and the seasonal high ground water table;

(ii) to ensure there will be an adequate area of ground with the appropriate soil type for the effluent land application area and reserve area when required;

(iii) to ensure there will be no restrictive soil horizon below the land application system;

(iv) to ensure there will be no barrier to horizontal soil soakage.

2.14 Soil Classification

Soils are to be assessed and categorized as specified in AS/NZS 1547 4.1 A-F

2.15 Appearance and Feeling of Various Soil Textural Classes

Table 8: Appearance and Feeling of Various Soil Textural Classes

| Soil Textural Class | Appearance and Feeling |
| --- | --- |
|  | Dry Soil | Moist Soil |
| Sand | Loose, single grains which feel gritty. Squeezed in the hand, the soil mass falls apart when the pressure is released. | Squeezed in the hand it forms a cast which crumbles when lightly touched. Does not form a ribbon between thumb and forefinger. |
| Loamy Sand | Loose, single grains, which feel gritty but enough fine particles to stain fingerprints in the palm of hand. | Squeezed in the hand. It forms a cast that crumble when touched and only bears very careful handling. |
| Sandy Loam | Aggregates are easily crushed. Very faint, velvety feeling initially, but as rubbing is continued; the gritty feeling of sand soon dominates. | Forms a cast that bears careful handling without breaking. Doesn't form a ribbon between thumb and forefinger. |
| Loam | Aggregates are crushed under moderate pressure; clods can be quite firm. When pulverised, loam has a velvety feel that becomes gritty with continued rubbing. | Cast can be handled quite freely without breaking. Slight tendency to ribbon between thumb and forefinger. Rubbed surface has a broken or rippled appearance. |
| Silt Loam | Aggregates are firm but may be crushed under moderate pressure. Clods are firm to hard. Smooth, flour-like feel dominates when soil is pulverised. | Cast can be handled very firmly without breaking. Tendency to ribbon between thumb and forefinger with some flaking, greasy feeling, moderately sticky. |
| Silty Clay Loam | Aggregates are very firm. Clods are hard to very hard. | Cast can be handled very firmly without breaking. Tendency to ribbon between thumb and forefinger with some flaking, greasy feeling, moderately sticky. |
| Silty Clay |  | Squeezed with proper moisture content into a long ribbon; sticky feel. |

2.16 Setbacks

Regulation 15 (8)

Setback standards are as follows:

The approved treatment unit and land application system shall be at least:

• 2m from any land boundary
• 3m from any building
• 15m from any surface water and groundwater well

Installers shall endeavour to ensure that all sewage systems comply with the setback requirements provided above except in cases where land is limited, in which case treatment shall be improved.

2.17 Design Specification of Land Application System

Trenches, beds, mounds and subsurface irrigation system are to be designed in accordance with the standards set in AS/NZS 1547:2000.

2.18 Drain laying Standards

Regulation 15 (7)

All drain laying shall be in accordance with the AS/NZS 3500 National plumbing and drainage code standards and the New Zealand Building Code El Surface Water and G13 Foul Water standards.

2.19 Treatment Unit Categories and Effluent Quality Standards

Regulation 15 (4)

As a guide, raw sewage has a biochemical oxygen demand (BOD5) and Total Suspendid Solids of TSS of 300 - 400 mg/litre and a faecal coliform count of 1010-107 cfu/100ml

Table 9: Treatment Unit Categories and Effluent Quality Standards

| Treatment level | Effluent standards |
| --- | --- |
| Primary treatment | BOD5 - 90% of samples taken over three test periods shall not exceed 180mg/litre and no sample shall exceed 200mg/litre TSS - 90% of samples taken over three test periods shall not exceed 80mg/litre and no sample shall exceed 100mg/litre FC - the median value shall be no more than 107 cfu/100ml and no sample shall exceed 108 cfu/100ml. |
| Secondary treatment | BOD5 - 90% of samples taken over three test periods shall not exceed 200mg/litre TSS - 90% of samples taken over three test periods shall not exceed 80mg/litre and no sample shall exceed 45mg/litre FC - Where disinfection is provided, the samples taken on each occasion shall have a thermotolerant coliform count not exceeding a median value of 10 organisms per 100ml with 80% of the samples containing less than 20 organisms per 100ml and no sample exceeding 100 organisms per 100ml. Where disinfection is not provided, the samples taken on each occasion shall have a thermotolerant coliform count not exceeding a median value of 104 organisms per 100ml with 80% of the samples containing less than 105 organisms per 100ml and no sample exceeding 106 organisms per 100ml. TN - 90% of samples taken over three test periods shall not exceed 40 mg/litre and no sample shall exceed 60 mg/litre Where chlorination is the disinfection process, the total chlorine concentration shall be greater than or equal to 0.5mg/litre in four out of five samples taken. |
| Advanced treatment | BOD5 - 90% of samples taken over three test periods shall not exceed 10mg/litre and no sample shall exceed 20mg/litre TSS-90% of samples taken over three test periods shall not exceed 10mg/litre and no sample shall exceed 20mg/litre FC - The samples taken on each occasion shall have a thermotolerant coliform count not exceeding a median value of 10 organisms per 100ml with 80% of the samples containing less than 20 organisms per 100ml and no sample exceeding 100 organisms per 100ml. TN - 90% of samples taken over three test periods shall not exceed 15mg/litre and no sample shall exceed 20mg/litre TP - 90% of samples taken over three test periods shall not exceed 5mg/litre and no sample shall exceed 10mg/litre Where chlorination is the disinfection process, the total chlorine concentration shall be greater than or equal to 0.5mg/litre in four out of five samples taken. |

2.20 Effluent outlet filters

Effluent outlet filters must reduce Total Suspended Solids to no more than 50mg/l. This performance data must be provided by an accredited independent testing agency.

Effluent outlet filters must have a filter aperture of no more than 3mm and a minimum surface area of 28,800mm2.

Servicing intervals of effluent outlet filters shall be specified by the manufacturer. The preferred period for servicing is once every three years.

2.21 Noise

The maximum permissible noise level with all equipment (except the alarm) operating shall be 40 dB (A) measured on fast response at a distance of lm from the nearest item of noise emitting equipment.

2.22 Septic Tank Construction Standards

Regulation 8

Septic tank manufacturers shall construct septic tanks to meet AS/NZS 1546.1:2008 On-site domestic wastewater treatment units Part 1: Septic tanks.

2.23 Sewage Discharge Standards

Regulation 14

Sewage shall not under any circumstances be discharged to surface water. Sewage shall not be discharged directly to groundwater but shall be treated and applied to land as outlined in this code.

3.0 Time Periods

3.1 Request for Sewage System Inspection - Regulation 21 (3) and 21 (5)

After receiving a request for sewage system inspection on the prescribed form, the Sanitary Inspector shall inspect the system on a day and time agreed between the inspector, owner and registered installer.

4.0 Registers

4.1 Register of Sanitary Professionals and Technicians - Regulation 7

4.1.1 Criteria for Installers and Servicing Agents

The registration of installers and servicing Agents shall not take effect until 1st October 2009. Until that time, the Sewage and Sanitation Board shall retain a list of Approved Installers and Servicing Agents who are qualified to install and service septic tanks and other sewage treatment systems.

The criteria for Approved Installers and Servicing Agents are:

1) A National Certificate in Drainlaying (Level 4) from an NZQA accredited institution* in New Zealand or a similar institution in Australia

AND

2) At least two years of practical experience supervised by a drainlayer registered in New Zealand or Australia

AND

3) Has completed a short course, set and approved by the Board, on the Public Health (Sewage) Regulations 2008 and the Public Health Sewage Code 2008 (the CET Sewage and Sanitation Course held in Rarotonga, Cook Islands 2006-2007 qualifies for this requirement)

Discretion Approval

Applicants who do not meet criteria 1) but who have a qualification in drainlaying from an institution outside of New Zealand or Australia may apply for discretionary approval. Applicants who do not meet criteria 2) and/or 3) may not be registered by the Sewage and Sanitation Board. Applications for discretionary approval are to include the following details:

1) Name
2) Contact details
3) Formal qualification with full contact details of the institution certifying the qualification
4) Details of professional registration (type of license, license number, name and full contact details of the authority issuing the license)
5) Membership of professional and/or trade bodies (if any) and their full contact details
6) Summary of experience in drain laying
7) Details of experience within the Cook Islands (if any)
8) Full contact details for three professional and/or industry referees
9) Full contact details for three clients for jobs completed within the last three years
10) Notarized copy of formal qualifications and birth certificate

The Sewage and Sanitation Board reserves the right to require the applicant to sit an assessment paper and/or to have their work assessed by a New Zealand/Australian Registered drainlayer.

A listing as an Approved Installer and/or Servicing Agent will become void upon 1st October 2009.

Registration of Installers and Servicing Agents (Septic Tanks)

After 1st October 2009, Public Health will only approve the installation of primary treatment systems (septic tanks) that are installed by Cook Islands Registered Installers of septic tanks. Furthermore, after 1st October 2009, only Cook Islands Registered Servicing Agents of primary treatment systems (septic tanks) will be permitted to service septic tanks, The criteria for Registered Installers and Servicing Agents of septic tanks are the same criteria used to determine Approved Installers and Servicing Agents (outlined in 1 - 3 above).

Registration for installers and servicing agents of septic tanks who receive registration on or after 1st October 2009 will be valid until 1st October 2010. Thereafter, annual renewal of registration will be required and will be due on the 1st October of each year.

Registration of Installers and Servicing Agents (Secondary/Advanced Sewage Treatment Systems)

After 1st October 2009, Public Health will only approve the installation of Secondary/Advanced treatment systems that are installed by Cook Islands Registered Installers of Secondary/Advanced treatment systems. Furthermore, after 1st October 2009, only Cook Islands Registered Servicing Agents of Secondary/Advanced treatment systems will be permitted to service Secondary/Advanced treatment systems. The criteria for Registered Installers of Secondary/Advanced treatment systems are the same criteria used to determine Approved Installers and Servicing Agents (outlined in 1 - 3 above) with the ADDITIONAL criterion which shall be:

4) Has been trained and certified by the manufacturers of the Secondary/Advanced treatment system as an installer and servicing agent for the respective model of that treatment system.

Registration for installers and Servicing Agents of Secondary/Advanced treatment systems who receive registration on or after 1st October 2009 will be valid until 1st October 2010. Thereafter, annual renewal of registration will be required and will be due on the 1st October of each year.

*accredited institutions which provide this qualification in New Zealand are:

Christchurch Polytechnic Institute of Technology
UniTec New Zealand
Waikato Institute of Technology
Wellington Institute of Technology
Plumbing, Gasfitting and Drainlaying ITO Ltd.

4.1.2 Criteria for the Registration of Inspectors

Between 31st January 2008 and 1st October 2009, the criteria for the registration of inspectors are:

1) The applicant has obtained a pass in the exams for the CET Sewage and Sanitation Course Category 1

AND

2) The applicant has submitted at least one CET Stage 3 project and received a pass for that project

AND

3) The applicant is able to demonstrate experience with and knowledge of the drainlaying and plumbing trade

Registration for inspectors who are registered during this period will be valid for 12 months from the date of approval.

After 1st October 2009, the criteria for the registration of inspectors are:

1) The applicant has a pass in the CET Sewage and Sanitation Course Category 1

AND

2) The applicant has a Certificate for Drainlaying Theory Assessment from an NZQA accredited institution in New Zealand or an equivalent institution in Australia or a qualification equivalent to the requirements set out by the Master Plumbers, Gasfitters and Drainlayers NZ Inc. Industry Training Organisation for a Certificate for Drainlaying Theory Assessment."

Registration for inspectors who are registered during this period will be valid for 12 months from the date of approval.

4.1.3 Criteria for the Registration of Designers

Between 31st January 2008 and 1st October 2009, the criteria for the registration of designers are:

1) The applicant has obtained a pass in the exams for the CET Sewage and Sanitation Course Category 2

AND

2) The applicant has submitted at least one CET Stage 3 project and received a pass for that project

AND

3) The applicant has an appropriate engineering or applied science degree or diploma

Registration for designers who are registered during this period will be valid for 12 months from the date of approval.

After 1st October 2009, the criteria for the registration of designers are:

1) The applicant has obtained a pass in the CET Sewage and Sanitation Course Category

AND

2 The applicant has an appropriate engineering or applied science degree or diploma

Registration for designers who are registered during this period will be valid for 12 months from the date of approval.

Exemptions:

There will be some applicants who will consider that they have qualifications and experience in sanitation equivalent to, or of a higher standard than, the qualifications specified above. The Board will consider applications from such professionals and tradespeople. The applicant will be required submit details of the qualifications and experience. Applications should be made to:

Health Planner (Sanitation)
Ministry of Health
PO Box 109
Rarotonga

The application is to include the following details:

1) Name
2) Contact details
3) CET or similar course(s) attended including year and venue of each course
4) Any other formal qualification with details of the institution certifying the qualification
5) Details of professional registration, if any
6) Details of any membership of professional and/or trade bodies
7) Summary of experience in sanitation engineering
8) Details of experience within the Cook Islands
9) Contact details for three professional and/or industry referees

The Board reserves the right to require the applicant to sit an assessment paper.

4.2 Register of Sewage Treatment Unit Designs - Regulation 9

4.2.1 Criteria for the Registration of Sewage Treatment Unit Designs

For the purpose of the Code, sewage management systems have been categorized as follows:

a. Dry sewage management systems - any waste system designed to manage domestic waste undiluted with flush water e.g. composting toilets

b. Wet sewage management systems - any waste system designed to manage domestic wastewater diluted with flush water, and there are many different types. This also includes greywater.

A sewage management system will normally consist of the following basic components:

• Source technologies (toilets, showers, washing machine, sinks etc)
• Treatment unit (septic tank, aeration unit, sand filter etc)
• Land application components (soak pit, trench, mound, subsurface irrigation field etc)

The regulations require

• The registration of Septic Tank Manufacturers (Reg 8)
• The registration of Sewage Treatment Unit Designs (Reg 9)

The criteria for registration of septic tanks are that the septic tanks be manufactured to the standards specified in AS/NZS 1546.1:2008 Septic Tanks and that the selection and application be in accordance with AS/NZS 1547:2000.

Primary, secondary and advanced treatment units are required to meet the effluent standards specified in Table 9.

4.2.2 AERATION TREATMENT PLANTS

Aeration treatment plants designed for individual homes are to meet the requirements specified in AS/NZS 1546.3:2008

4.2.3 Applications for the Registration of Sewage Treatment Unit Designs - Regulation 9 (2)

Applications for the Registration of Secondary or Advanced Treatment Systems shall consist of:

(a) a description of the treatment process used by the sewage system;

(b) mechanical and electrical specifications and other technical specifications if applicable;

(c) performance of the treatment unit in terms of effluent BOD5, suspended solids, faecal coliforms, total nitrogen and total phosphorus from an accredited independent testing agency;

(d) design criteria for maximum short-term peak hydraulic loading capacity of the treatment unit;

(e) information on emergency storage capacity;

(f) evidence of resilience to variable loading (in terms of influent quantity and quality);

(g) a description of alarm system used;

(h) an action plan and impact of power failure;

(i) guarantee/warranty details;

(j) information on recommended land application systems in accordance with the Public Health Sewage Code;

(k) an indication of the system's power consumption;

(l) an indication of the level of noise (in decibels) produced by the system;

(m) names and addresses of companies that manufacture the tanks and land application system and any pumps, blowers or rotating disks if applicable;

(n) a copy of the operation and maintenance manual provided to the property owner and servicing agent;

(o) details of certification by an independent certifier. The certifier should be required to provide their CV and validate their competence in wastewater engineering;

(p) a declaration of whether the sewage system is designed to meet the requirements of a Secondary Treatment System or Advanced Treatment System, as defined in the Public Health Sewage Code; and

(q) any other information that may be required by the Board..

The registration process involves:

1. The submission of an application for registration to the Health Planner (Sanitation) at Public Health, PO Box 109, Rarotonga.

2. Review by the Health Planner (Sanitation) and two independent sanitary engineers

3. Consideration of advice and possible endorsement by the Sewage and Sanitation Board.

The criteria for registration are:

1. Certification of the treatment unit by an independent certifier

2. The use of a scientifically proven and peer-reviewed treatment process

3. Performance details in terms of BOD5 in mg/l, suspended solids in mg/l, faecal coliform bacteria (coliform forming units per 100ml), total nitrogen (mg/l) and total phosphorus (mg/l). Performance data must be provided by an accredited independent testing agency.

4. Compliance with relevant AS/NZS engineering standards

5. Resilience to changes in influent loading (in terms of influent quantity and quality)

6. Ease of installation and servicing

7. Capacity for emergency storage in case of power failure

8. Low power consumption and operation and maintenance costs

9. Low noise, low risk of odour, low risk of insect and pest breeding

10. Detailed operation and maintenance manual

11. The presence of at least two servicing agents in-country who are certified to service the system.

12. Contact details of independent referees

4.3 Register of Septic Tank Manufacturers - Regulation 8

4.3.1 Criteria for the Registration of Septic Tank Manufacturers

To be registered as a Septic Tank Manufacturer the manufacturer must demonstrate that they can consistently manufacture septic tanks according to the AS/NZS 1546.1:2008 Septic Tank standards.

5.0 Reports

5.1 Abandonment or Disconnection Plan - Regulation 31

An Abandonment or disconnection plan shall outline the following:

1) How the developer of a new sewage treatment system will manage wastewater that is normally treated by the abandoned sewage system;

2) How the components of the system will be dismantled and waste material managed;

3) How the site will be rehabilitated and left in a safe, clean and environmentally satisfactory manner.

5.2 Operation and Maintenance Manual-Regulation 29

An Operation and Maintenance manual for a Secondary or Advanced Treatment System shall contain:

(i) operation and maintenance instructions for each pump station and treatment unit or process under normal and emergency conditions such as power outage and equipment malfunction;

(ii) operation and maintenance instructions for the land application system including procedures for purging or chemical shock loading to prevent or eliminate biological growth in a subsurface disposal system

(iii) a list of required sampling frequencies and analyses to be conducted by the operator;

(iv) a checklist of troubleshooting, corrective, and preventative measures to be taken to maintain process control and treatment performance;

(v) a checklist of start-up procedures;

(vi) applicable Cook Islands effluent requirements;

(vii) instructions on the collection and disposal of sewage sludge;

(viii) a summary of labour requirements needed to operate and maintain the sewage system;

(ix) a list of critical parts of the sewage system;

(x) as built drawings of the sewage system;

(xi) a list of required daily activities, checks and observations;

(xii) logs or report forms for all operation and maintenance activities performed;

(xiii) results of all discharge sampling undertaken on the system;

(xiv) all necessary flow schematic diagrams with details of piping and valuing;

(xv) a plot plan of the sewage system and site including all collection lines and equipment;

(xvi) details on all safety equipment at the sewage system site, any applicable spare parts, maintenance and operation instructions;

(xvii) details on all monitoring equipment including spare parts, maintenance and operating instructions;

(xviii) names and addresses of suppliers of all spare parts; and

(xix) contingency plans to ensure the continued operation of the system in the event of any natural or man-made disaster.